## 1. Master Dashboard
RECOMMENDATIONS FOR BETTER ENERGY EFFICIENCY — MASTER DASHBOARD
All 16 Recommendations ¦ Auto-Calculated Savings, ROI, Payback, CO₂ Reduction ¦ A.Y. 2026–27
Sl. | Recommendation | Category | Est. Savings (kWh/yr) | Est. Cost (₹) | Tariff (₹/kWh) | Annual Monetary Savings (₹) | Payback Period (Years) | 5-Year Net Savings (₹) | 10-Year Net Savings (₹) | CO₂ Reduction (tons/yr) | Responsible Department
1 | Replace old motors with energy-efficient motors | Equipment Upgrade | 20000 | 500000 | 8 | 160000 | 3.125 | 300000 | 1100000 | 16.4 | Maintenance Dept.
2 | Replace conventional chokes with electronic chokes | Equipment Upgrade | 5000 | 100000 | 8 | 40000 | 2.5 | 100000 | 300000 | 4.1 | Electrical Dept.
3 | Use motion sensors in corridors & toilets | Automation & IoT | 12000 | 150000 | 8 | 96000 | 1.5625 | 330000 | 810000 | 9.84 | Energy Audit Committee
4 | Replace all FTLs with LED lights | Equipment Upgrade | 36000 | 400000 | 8 | 288000 | 1.3889 | 1040000 | 2480000 | 29.52 | Electrical Dept.
5 | Replace laser printers with inkjet printers | Equipment Upgrade | 4000 | 80000 | 8 | 32000 | 2.5 | 80000 | 240000 | 3.28 | IT & Admin
6 | Replace CRT monitors with LCD/LED monitors | Equipment Upgrade | 10000 | 120000 | 8 | 80000 | 1.5 | 280000 | 680000 | 8.2 | IT & Admin
7 | Replace old UPS with energy-efficient UPS | Equipment Upgrade | 8000 | 250000 | 8 | 64000 | 3.9062 | 70000 | 390000 | 6.56 | IT/Infrastructure
8 | Regular maintenance of batteries | Maintenance | 3000 | 20000 | 8 | 24000 | 0.83333 | 100000 | 220000 | 2.46 | Maintenance Dept.
9 | Automate appliances with smart assistants | Automation & IoT | 2000 | 50000 | 8 | 16000 | 3.125 | 30000 | 110000 | 1.64 | Energy Audit Committee
10 | Increase natural lighting | Building Design | 1500 | 30000 | 8 | 12000 | 2.5 | 30000 | 90000 | 1.23 | Infrastructure Office
11 | Switch out incandescent lights | Equipment Upgrade | 6000 | 50000 | 8 | 48000 | 1.0417 | 190000 | 430000 | 4.92 | Electrical Dept.
12 | Unplug battery chargers when not in use | Behavioural | 1000 | 10000 | 8 | 8000 | 1.25 | 30000 | 70000 | 0.82 | All Staff & Students
13 | Automate thermostat by time of day | Automation & IoT | 7000 | 70000 | 8 | 56000 | 1.25 | 210000 | 490000 | 5.74 | Maintenance Dept.
14 | Set computers to sleep/hibernate mode | Behavioural | 5000 | 40000 | 8 | 40000 | 1 | 160000 | 360000 | 4.1 | IT Dept.
15 | Use electric kettles instead of microwaves | Equipment Upgrade | 2500 | 30000 | 8 | 20000 | 1.5 | 70000 | 170000 | 2.05 | Hostel/Guest House
16 | Install low-flow showerheads in hostels | Building Design | 4000 | 25000 | 8 | 32000 | 0.78125 | 135000 | 295000 | 3.28 | Hostel Administration
| GRAND TOTAL |  | 127000 | 1925000 |  | 1016000 | 1.8947 | 3155000 | 8235000 | 104.14
| % of Total Savings |  | 100 | 100 |  | 100 |  |  |  | 100
KEY INSTITUTIONAL METRICS — Auto-Calculated
Total Annual Energy Savings (kWh) | [5 empty] | 127000
Total Annual Monetary Savings (₹) | [5 empty] | 1016000
Total Implementation Cost (₹) | [5 empty] | 1925000
Overall Payback Period (Years) | [5 empty] | 1.8947
5-Year Net Institutional Savings (₹) | [5 empty] | 3155000
10-Year Net Institutional Savings (₹) | [5 empty] | 8235000
Annual CO₂ Reduction (tons) | [5 empty] | 104.14
Equivalent Trees Planted per Year | [5 empty] | 4733.6364
% Energy Reduction (if base = 500,000 kWh) | [5 empty] | 25.4
Highest-Impact Recommendation | [5 empty] | Replace all FTLs with LED lights
Fastest Payback Recommendation | [5 empty] | Install low-flow showerheads in hostels

## 2. Category Analysis
CATEGORY-WISE ENERGY EFFICIENCY ANALYSIS
Grouped by: Equipment Upgrade ¦ Automation & IoT ¦ Maintenance ¦ Building Design ¦ Behavioural
# | Category | No. of Recommendations | Total Savings (kWh/yr) | Total Cost (₹) | Total Annual Savings (₹) | Avg Payback (Years) | % of Total kWh Savings | CO₂ Reduction (tons/yr)
1 | Equipment Upgrade | 8 | 91500 | 1530000 | 732000 | 2.0902 | 72.0472 | 75.03
2 | Automation & IoT | 3 | 21000 | 270000 | 168000 | 1.6071 | 16.5354 | 17.22
3 | Maintenance | 1 | 3000 | 20000 | 24000 | 0.83333 | 2.3622 | 2.46
4 | Building Design | 2 | 5500 | 55000 | 44000 | 1.25 | 4.3307 | 4.51
5 | Behavioural | 2 | 6000 | 50000 | 48000 | 1.0417 | 4.7244 | 4.92
| TOTAL | 16 | 127000 | 1925000 | 1016000 | 1.8947 | 100% | 104.14

## 3. Department Tracker
DEPARTMENT-WISE RESPONSIBILITY & IMPLEMENTATION TRACKER
Auto-linked from Master Dashboard ¦ Tracks each department's assigned savings target and cost responsibility
# | Responsible Department | No. of Recommendations | Total Savings (kWh/yr) | Total Cost (₹) | Annual Monetary Savings (₹) | Avg Payback (Years) | % of Total Savings
1 | Maintenance Dept. | 3 | 30000 | 590000 | 240000 | 2.4583 | 23.622
2 | Electrical Dept. | 3 | 47000 | 550000 | 376000 | 1.4628 | 37.0079
3 | Energy Audit Committee | 2 | 14000 | 200000 | 112000 | 1.7857 | 11.0236
4 | IT & Admin | 2 | 14000 | 200000 | 112000 | 1.7857 | 11.0236
5 | IT/Infrastructure | 1 | 8000 | 250000 | 64000 | 3.9062 | 6.2992
6 | Infrastructure Office | 1 | 1500 | 30000 | 12000 | 2.5 | 1.1811
7 | All Staff & Students | 1 | 1000 | 10000 | 8000 | 1.25 | 0.7874
8 | IT Dept. | 1 | 5000 | 40000 | 40000 | 1 | 3.937
9 | Hostel/Guest House | 1 | 2500 | 30000 | 20000 | 1.5 | 1.9685
10 | Hostel Administration | 1 | 4000 | 25000 | 32000 | 0.78125 | 3.1496
| TOTAL | 16 | 127000 | 1925000 | 1016000 | 1.8947 | 100%

## 4. Implementation Plan
PHASED IMPLEMENTATION PLAN & PROGRESS TRACKER
Phase 1: Quick Wins (0–6 months) ¦ Phase 2: Medium-Term (6–18 months) ¦ Phase 3: Major Investments (18–36 months)
# | Recommendation | Phase (1/2/3) | Priority (H/M/L) | Start Date | Target Date | Est. Cost (₹) | Actual Cost (₹) | % Complete | Status | Remarks
1 | Replace old motors with energy-efficient motors | 1 | H |  |  | 500000
2 | Replace conventional chokes with electronic chokes | 1 | M |  |  | 100000
3 | Use motion sensors in corridors & toilets | 2 | H |  |  | 150000
4 | Replace all FTLs with LED lights | 2 | H |  |  | 400000
5 | Replace laser printers with inkjet printers | 1 | M |  |  | 80000
6 | Replace CRT monitors with LCD/LED monitors | 1 | M |  |  | 120000
7 | Replace old UPS with energy-efficient UPS | 3 | H |  |  | 250000
8 | Regular maintenance of batteries | 1 | H |  |  | 20000
9 | Automate appliances with smart assistants | 2 | M |  |  | 50000
10 | Increase natural lighting | 3 | L |  |  | 30000
11 | Switch out incandescent lights | 1 | H |  |  | 50000
12 | Unplug battery chargers when not in use | 1 | L |  |  | 10000
13 | Automate thermostat by time of day | 2 | M |  |  | 70000
14 | Set computers to sleep/hibernate mode | 1 | M |  |  | 40000
15 | Use electric kettles instead of microwaves | 1 | L |  |  | 30000
16 | Install low-flow showerheads in hostels | 2 | M |  |  | 25000
Phase-wise Summary — Auto-Calculated
| Phase | Count |  |  |  | Est. Cost (₹) | Actual Cost (₹) | Avg % Complete
| Phase 1: Quick Wins (0–6 months) | 9 |  |  |  | 950000 | 0 | 0
| Phase 2: Medium-Term (6–18 months) | 5 |  |  |  | 695000 | 0 | 0
| Phase 3: Major Investments (18–36 months) | 2 |  |  |  | 280000 | 0 | 0

## 5. Technical Details
DETAILED TECHNICAL SPECIFICATIONS & JUSTIFICATION
Technical rationale, before/after comparison, and quantified savings per recommendation
# | Recommendation | Technical Description & Rationale | Before (Old System) | After (New/Upgraded) | Quantified Improvement | Standards / References
1 | Replace old motors | Old induction motors: 70–80% efficient, excess heat, high slip | Standard: IE1 (70–80%) | Upgrade: IE2/IE3 (90–95%) | 10–15% power reduction per motor | IS 12615, IEC 60034-30
2 | Replace chokes | Magnetic ballast: 10–15W loss/lamp, low power factor (0.5) | Magnetic choke: 10–15W loss | Electronic choke: <1W loss | 15–20% energy saving, PF >0.9 | IS 13021, IEC 61347
3 | Motion sensors | Corridors/toilets lit 24/7 unnecessarily; PIR sensors detect occupancy | Constant ON: 100% duty | Sensor: 60–70% duty | 30–40% lighting savings | IS 4648, ECBC 2017
4 | FTL to LED | FTL (36W+choke) = 46W vs LED tube (18W); better CRI, no flickering | FTL: 46W per tube | LED: 18W per tube | 60–65% reduction per point | IS 16102, IEC 62560
5 | Laser to inkjet | Laser fuser heats to 200°C (500–1000W); inkjet uses 30–50W | Laser: 500–1000W peak | Inkjet: 30–50W | 80–90% energy reduction | Energy Star, BEE Label
6 | CRT to LCD/LED | CRT ~100W, heavy, poor ergonomics; LCD/LED 25–40W, thin, crisp | CRT: ~100W | LCD/LED: 25–40W | 60–75% reduction | Energy Star, BIS
7 | Old to efficient UPS | Old UPS: 70–80% conversion; modern >95%; less heat waste | Old UPS: 70–80% eff. | New UPS: >95% eff. | 15–25% standby savings | IS 16242, IEC 62040
8 | Battery maintenance | Neglected batteries: sulfation, leakage, early failure, energy waste | Unmaintained: 60–70% capacity | Maintained: 90–95% capacity | 20–30% efficiency gain | IS 1651, IEEE 1188
9 | Smart assistants | Devices left ON by humans; IoT timers enforce schedules automatically | Manual: human error prone | Auto: scheduled ON/OFF | Eliminates phantom loads | IoT Standards, BIS
10 | Natural lighting | Dark corridors lit artificially; reflective surfaces redirect daylight | No daylight harvesting | Mirrors, light paint, skylights | Reduces daytime lighting 30–50% | NBC 2016, ECBC 2017, IGBC
11 | Incandescent to LED | Incandescent: 10% light / 90% heat; extreme inefficiency | Incandescent: 60–100W | LED: 7–12W | 85–90% energy reduction | IS 16102, BEE Star
12 | Unplug chargers | Idle chargers draw 0.5–2W each (vampire load); institutional scale adds up | Plugged in: 0.5–2W idle | Unplugged: 0W | Eliminates vampire load | Awareness campaign
13 | Smart thermostat | Manual AC: full power all day; smart adjusts by schedule/occupancy | Manual: constant set-point | Smart: adaptive schedule | 10–15% HVAC savings | BEE, ECBC 2017
14 | Computer sleep mode | Idle desktop: 50–100W; sleep: 1–3W; hibernate: <1W | Idle ON: 50–100W | Sleep: 1–3W | ~95% idle reduction | Energy Star, IT Policy
15 | Kettles vs microwaves | Kettle: 80–90% direct heating; microwave: scattered, less efficient | Microwave: 50–65% eff. | Kettle: 80–90% eff. | 20–30% energy savings for water heating | BIS, Energy Star
16 | Low-flow showerheads | Standard: 12–15 L/min; low-flow: 6–8 L/min; halves hot water demand | Standard: 12–15 L/min | Low-flow: 6–8 L/min | 50% hot water energy savings | IS 6392, WaterSense

## 6. Before vs After
BEFORE vs AFTER ENERGY COMPARISON — QUANTIFIED IMPACT
Auto-calculated: Enter 'Before' consumption → formulas compute 'After', Savings, Cost Reduction & CO₂ impact
# | Recommendation | Before (kWh/yr) | After (kWh/yr) | Savings (kWh/yr) | % Reduction | Annual Cost Savings (₹) | CO₂ Saved (tons/yr)
1 | Replace old motors with energy-efficient motors | 160000 | 140000 | 20000 | 12.5 | 160000 | 16.4
2 | Replace conventional chokes with electronic chokes | 28571 | 23571 | 5000 | 17.5003 | 40000 | 4.1
3 | Use motion sensors in corridors & toilets | 34286 | 22286 | 12000 | 34.9997 | 96000 | 9.84
4 | Replace all FTLs with LED lights | 55385 | 19385 | 36000 | 64.9995 | 288000 | 29.52
5 | Replace laser printers with inkjet printers | 4706 | 706 | 4000 | 84.9979 | 32000 | 3.28
6 | Replace CRT monitors with LCD/LED monitors | 15385 | 5385 | 10000 | 64.9984 | 80000 | 8.2
7 | Replace old UPS with energy-efficient UPS | 40000 | 32000 | 8000 | 20 | 64000 | 6.56
8 | Regular maintenance of batteries | 12000 | 9000 | 3000 | 25 | 24000 | 2.46
9 | Automate appliances with smart assistants | 13333 | 11333 | 2000 | 15.0004 | 16000 | 1.64
10 | Increase natural lighting | 3750 | 2250 | 1500 | 40 | 12000 | 1.23
11 | Switch out incandescent lights | 6818 | 818 | 6000 | 88.0023 | 48000 | 4.92
12 | Unplug battery chargers when not in use | 10000 | 9000 | 1000 | 10 | 8000 | 0.82
13 | Automate thermostat by time of day | 56000 | 49000 | 7000 | 12.5 | 56000 | 5.74
14 | Set computers to sleep/hibernate mode | 12500 | 7500 | 5000 | 40 | 40000 | 4.1
15 | Use electric kettles instead of microwaves | 10000 | 7500 | 2500 | 25 | 20000 | 2.05
16 | Install low-flow showerheads in hostels | 8000 | 4000 | 4000 | 50 | 32000 | 3.28
| TOTAL | 470734 | 343734 | 127000 | 26.9791 | 1016000 | 104.14

## 7. Carbon Impact
ENVIRONMENTAL & CARBON IMPACT — ALL 16 RECOMMENDATIONS
Auto-linked: CO₂, SO₂, NOx reduction + lifetime projections ¦ Indian grid: 0.82 tCO₂/MWh
# | Recommendation | Savings (kWh/yr) | CO₂ Avoided (tons/yr) | SO₂ Avoided (kg/yr) | NOx Avoided (kg/yr) | Trees Equivalent/yr
1 | Replace old motors with energy-efficient motors | 20000 | 16.4 | 100 | 60 | 745.4545
2 | Replace conventional chokes with electronic chokes | 5000 | 4.1 | 25 | 15 | 186.3636
3 | Use motion sensors in corridors & toilets | 12000 | 9.84 | 60 | 36 | 447.2727
4 | Replace all FTLs with LED lights | 36000 | 29.52 | 180 | 108 | 1341.8182
5 | Replace laser printers with inkjet printers | 4000 | 3.28 | 20 | 12 | 149.0909
6 | Replace CRT monitors with LCD/LED monitors | 10000 | 8.2 | 50 | 30 | 372.7273
7 | Replace old UPS with energy-efficient UPS | 8000 | 6.56 | 40 | 24 | 298.1818
8 | Regular maintenance of batteries | 3000 | 2.46 | 15 | 9 | 111.8182
9 | Automate appliances with smart assistants | 2000 | 1.64 | 10 | 6 | 74.5455
10 | Increase natural lighting | 1500 | 1.23 | 7.5 | 4.5 | 55.9091
11 | Switch out incandescent lights | 6000 | 4.92 | 30 | 18 | 223.6364
12 | Unplug battery chargers when not in use | 1000 | 0.82 | 5 | 3 | 37.2727
13 | Automate thermostat by time of day | 7000 | 5.74 | 35 | 21 | 260.9091
14 | Set computers to sleep/hibernate mode | 5000 | 4.1 | 25 | 15 | 186.3636
15 | Use electric kettles instead of microwaves | 2500 | 2.05 | 12.5 | 7.5 | 93.1818
16 | Install low-flow showerheads in hostels | 4000 | 3.28 | 20 | 12 | 149.0909
| ANNUAL TOTAL | 127000 | 104.14 | 635 | 381 | 4733.6364
| 10-YEAR LIFETIME | 1270000 | 1041.4 | 6350 | 3810 | 47336.3636
| 25-YEAR LIFETIME | 3175000 | 2603.5 | 15875 | 9525 | 118340.9091

## 8. Data Quality Audit
ENERGY EFFICIENCY RECOMMENDATIONS — DATA QUALITY & AUDIT CHECKLIST
20-point verification for data accuracy, financial integrity & implementation readiness
# | Quality Check | Description | Status (✓/✗/IP) | Date | Reviewer
1 | Baseline energy consumption | Institutional baseline verified from utility bills for 12 consecutive months (kWh)
2 | Appliance inventory accuracy | Appliance counts verified against physical inspection or departmental inventory registers
3 | Wattage ratings verified | Rated wattage for each appliance type cross-checked against nameplate or BEE database
4 | Savings estimates methodology | kWh savings calculated using accepted engineering formulas, not estimates or vendor claims
5 | Cost estimates sourced | Implementation costs verified against minimum 3 vendor quotations or GeM portal rates
6 | Tariff rate current | Electricity tariff matches latest DISCOM tariff order for institutional HT/LT category
7 | Payback calculation | Payback = Cost ÷ Annual Savings; verified manually for all 16 recommendations
8 | CO₂ emission factor | CEA CO₂ Baseline Database (0.82 tCO₂/MWh) or latest published figure used consistently
9 | Category classification | Each recommendation correctly classified (Equipment/Automation/Maintenance/Building/Behavioural)
10 | Department assignment | Responsible departments confirmed by institutional authority; no overlaps or gaps
11 | Phase assignment rationale | Phase 1/2/3 assignment based on cost, complexity, and institutional readiness assessment
12 | Priority assignment | H/M/L priorities verified against energy audit report recommendations
13 | Technical specifications | Before/After technical comparisons verified against IS/IEC/BIS standards cited
14 | BEE star rating reference | Star ratings for applicable appliances verified from BEE label database
15 | Double-counting check | No savings counted twice across overlapping recommendations (e.g., FTL→LED and incandescent→LED)
16 | Sensitivity analysis | Key assumptions (tariff, usage hours, degradation) tested with ±10% variation
17 | Measurement & Verification plan | M&V protocol defined for post-implementation savings verification (IPMVP Option A/B)
18 | Institutional approval | Energy efficiency implementation plan approved by competent institutional authority
19 | Budget allocation confirmed | Budget allocated in institutional financial plan for all three implementation phases
20 | Annual review mechanism | Annual review and reporting mechanism established for tracking actual vs. projected savings
Checks Passed |  |  | 0
Completion Rate (%) |  |  | 0